|  | 无锡海潮新能源科技有限公司Wuxi Hadron New Energy Tech Co.Ltd | VER: A1 |
| --- | --- | --- |
|  | 地址：江苏省江阴市城东金山路201号数码港B栋2楼 TEL：86（0）510-86257982 FAX：86（0）510-84060182 | DATE:2023/03/28 |
| 12.8V lithium-ion battery pack specification 12.8V锂离子电池组规格书 Product Name/产品名称： 12.8V后备电源 MODEL/型号:12.8V280Ah Prepared By/Date 编 制/日 期; Checked By/Date 审 核/日 期; Approved By/Date 批 准/日 期. 20230328; 20230328; 20230328. Customer Approval 客户批准; Signature 确认; Date 日期. Company Name： 公司名称：. Company Stamp： 客户印章：. --- Great Power Confidential --- --- 保密文件 --- |
| Amendment Records （修正记录）. Edition (版 本); Description （记 述）; Prepared by （编 制）; Approved by （批 准）; Date （日 期）. A1; First Publish; 曾璐; 龚建平; 20230328. |
| 1 Scope（适用范围） This specification is applied to the reference battery in this Specification that manufactured by Wuxi Hadron Energy Co., Ltd. 本规格书适用于本书中所提及的、无锡海潮能源有限公司制造的电池。 2 Product Specification（产品技术规格） Table 1 (表 1) No. (序号); Item （项目）; General Parameter (常规参数); Remark （备注）. 1; Product name & number (产品名称及产品物料号); 12.8V lithium battery pack 12.8V锂电池组; Lithium iron phosphate cells （磷酸铁锂电芯）. 2; Rated Capacity （额定容量）; Typical （标称容量）; 280000mAh; Standard discharge（0.2C5A) after Standard charge （标准充电后0.2C5A标准放电）. Minimum (最小容量); 260000mAh. 3; Nominal Voltage （正常电压）; 12.8V; Mean Operation Voltage （即工作电压）. 4; Voltage at end of Discharge （放电终止电压）; 11V; Discharge Cut-off Voltage （放电截止电压）. 5; Charging Voltage (充电电压); 14.6V. 6; Standard charge （标准充电）; Constant Current 20A Constant Voltage 14.6V 1A cut-off （持续电流：20A 持续电压：14.6V 截止电流： 1A）; Constant Current 20A Constant Voltage 14.6V cut-off 1A （持续电流：20A 持续电压：14.6V 截止电流：1A. 7; Standard discharge （标准放电）; Constant current 50A end voltage 11V （持续电流：50A 截止电压：11V）; Constant current 50A end voltage 11V （持续电流：50A 截止电压：11V）. 8; Maximum Continuous Charge Current (最大充电持续电流); 40A. 9; Maximum Continuous Discharge Current （最大放电持续电流）; 60A. |
| Continuous the table 1 (续 表1) No. (序号); Item （项目）; General Parameter (常规参数); Remark （备注）. 10; Charge and discharge restrictions （充放电限制条件）; It can be charged when discharged, and it can be charged when discharged （放电时可以充电，放电时可以充电）; Common port for charge and discharge (充放电同口). 11; Temperature protection （温度保护）; Discharge temperature protection ：60±5℃ 放电温度保护：60±5℃ Recovery state：55±5℃ 恢复状态：55±5℃; Temperature sensor, Automatic recovery （温度传感器，自动恢复）. Under-Temperature Discharge ：-20±5℃ 放电低温度保护：-20±5℃ Recovery state：-5±5℃ 恢复状态：-5±5℃. Charge temperature protection：45±3℃ 充电温度保护：45±3℃ Recovery state：40±3℃ 恢复状态：40±3℃. Charge low temperature protection：0±3℃ 充电低温保护：0±3℃ Recovery state：2±3℃ 恢复状态：2±3℃. 12; Solar charging （太阳能充电）; Solar spike charging voltage ≤14.6V 最大充电电压≤14.6V. 13; Operation Temperature Range （工作温度范围）; Charge（充电）: 0~40℃; 60±25%R.H. PACK （电池组储存湿度范围）. Discharge（放电）: -10~50℃. 14; Storage Temperature Range （储存温度范围）; Less than 1 year: -20~23℃ （小于一年：-20~23℃）; 60±25%R.H. at the shipment state （出货状态时的湿度范围）. less than 3 months: -20~40℃ （小于3个月：-20~40℃）. Less than 7 day : -20~60℃ （小于7天：-20~60℃）. |
| 3．保护板技术规格BMS specification 3．1适用范围using scope： 本规格书适用于由本公司所设计生产的 12.8V 280Ah 锂电池组保护板。 This specification is used for the pack 12.8V 280Ah BMS of our company。 3．2技术参数electric features： 环境温度：25 ºC Item; Content; Criterion. Over charge Protection; Over charge detection voltage; 3.65±0.025V. Secondary overcharge detection voltage; 3.70 0.025. Over charge detection delay time; 1.0±0.5Sms. Over charge release voltage; 3.60±0.05V. Secondary Over charge release voltage; 3.550.05V. Over discharge protection; Over discharge detection voltage; 2.75±0.08V. Over discharge detection delay time; 100±50ms. Over discharge release voltage; 2.9±0.1V. Over current protection; Over current detection current 1; 150±1A. Over current detection delay time1; 1±0.5s. Over current detection current 2; 200±2A. Over current detection delay time2; 20±10ms. Release condition; unplugged to cut load and plugged the Battery Pack. Short protection; Detection condition; Exterior short circuit. Release condition; Cut short circuit. Short circuit detection delay time; 600μsMaX. Current consumption; Current consume in normal operation; 20mAMaX. |
| 4. Initial Performance Test（初始性能测试） Table 2（表 2） Item （项目）; Test Method and Condition （测试方法及条件）; Requirements （要求）. - Open-Circuit Voltage （开路电压）; The open-circuit voltage shall be measured within 24 hours after standard charge. （标准充电后24小时内测量开路电压）; ≥13.4V. - Minimal Rated Capacity (最小额定容量); The capacity on 0.2C5A discharge till the voltage tapered to 11V shall be measured after rested for 30min then finish standard charge. (标准充电后，搁置30min，测量0.2C放电至11V截止电压所放出的容量); Discharge Capacity （放电容量） ≥260000mAh. Temperature Dependence of discharge capacity（放电温度特性） The battery is charged according to the standard regulations. To discharge at the temperature of Table 3, the battery must first be left at this test temperature for 3 hours. The discharge capacity at each temperature should not be less than the requirements of Table 3. 电池按标准规定充电。按表3的温度中放电，电池必须先在该试验温度中放置3个小时。在每一个温度中的放电容量应不小于表3的要求。 Table 3 （表3） Discharge Temperature （放电温度）; -10℃; 0℃; 23℃; 60℃. Discharge Capacity（0.2 C5A） （放电容量/0.2 C5A）; 50%; 75%; 100%; 95%. |
| Cycle Life and Leakage-Proof（循环寿命及漏液试验） Table 4（表4） No. （序号）; Item （项目）; Criteria （标准）; Test Conditions （测试条件）. 1; Cycle Life （循环寿命）; Higher than 80% of the Initial Capacities of the Cells （初始容量的70%）; Carry out 4000cycle Charging/Discharging in the below condition. ◆Charge: Standard Charge ◆Discharge: 0.2C5A to 11 V ◆Rest Time between charge/discharge:30min. ◆Temperature:20±5℃ 循环4000次 充放电按以下条件： ◆充电: 标准充电 ◆放电: 0.2 C5A放至11V ◆搁置:30min. ◆温度:20±5℃. 2; Leakage-Proof （漏液试验）; No leakage (visual inspection) （没有漏液/目测）; After full charge with standard charge, store at 60±3℃, 60±10%RH for 1 month. 标准充电条件下充满电后在温度60±3℃，湿度60±10%RH下储存一个月. - Mechanical characteristics and Safety Test（安全测试及机械特性） Table 5（表5） (Mechanical characteristics) No. (序号); Items （项目）; Test Method and Condition （测试方法及条件）; Criteria （标准）. 1; Vibration Test 振动测试; After standard charging, fixed the cell to vibration table and subjected to vibration cycling that the frequency is to be varied at the rate of 1Hz per minute between 10Hz an 55Hz, the excursion of the vibration is 1.6mm. The pack shall be vibrated for 30 minutes per axis of XYZ axes. 将标准充电后的电池组固定在振动台上，沿X、Y、Z三个方向各振动30分钟，振幅1.6mm，振动频率为10Hz~55Hz，每分钟变化1Hz。; No leakage 无泄漏 No fire 不起火. 2; Drop Test 跌落测试; The packl is to be dropped from a height of 1 meter twice onto concrete ground. 将标准充电后的电池组从1米高度跌落至混凝土地面2次; No explosion, No fire, no leakage. 无爆炸、无起火 、无泄漏. |
| Table 6（表 6） (Safety Test) Item （项目）; Battery Condition （电池要求）; Test Method （测试方法）; Requirements （要求）. Crush （挤压试验）; Fresh, Fully charged （充满电的新电池）; Crush between two flat plates. Applied force is about 13kN(1.72Mpa) for 30min. （电池放置在两块平面金属板间，施加13KN（1.72Mpa）的作用力，且持续保持30分钟）; No explosion, No fire (无起火无爆炸). Short Circuit （短路试验 20℃）; Fresh, Fully charged （充满电的新电池）; Each test sample battery, in turn, is to be short- circuited by connecting the (+) and (-) terminals of the battery with a Cu wire having a maximum resistance load of 0.1Ω.Tests are to be conducted at room temperature(20±2℃ ). （在常温下约20±2℃依次把每个样品电池的正负极用铜线连接起来使电池外部短路--线路总电阻不超过0.1Ω）; No explosion, No fire The Temperature of the surface of the Cells are lower than 150℃ (无起火无爆炸 电池表面温度应低于150℃). Short Circuit （短路试验 60℃）; Fresh, Fully charged （充满电的新电池）; Each test sample battery, in turn, is to be short- circuited by connecting the (+) and (-) terminals of the battery with a Cu wire having a maximum resistance load of 0.1Ω.Tests are to be conducted at temperature(60±2℃ ). （在常温下约60±2℃依次把每个样品电池的正负极用铜线连接起来使电池外部短路--线路总电阻不超过0.1Ω）; No explosion, No fire The Temperature of the surface of the Cells are lower than 150℃ (无起火无爆炸 电池表面温度应低于150℃). Forced Discharge （过放试验）; Fresh, Fully charged （充满电的新电池）; Discharge at a current of 150A for 2.5h. （以150A 的电流放电2.5小时）; No explosion, No fire (无起火无爆炸). |
| 6. CAUTIONS IN USE(谨慎使用) To ensure proper use of the battery please read the manual carefully before using it. （为确保正确使用电池，使用前请仔细阅读本细则） . Handling（电池操作） - Do not expose to, dispose of the battery in fire.（不要靠近和放置电池于火中） - Do not put the battery in a charger or equipment with wrong terminals connected. （在充电器或设备仪器中不要把电池接错电极） - Avoid shorting the battery（避免电池短路） - Avoid excessive physical shock or vibration.（避免电池过多的物理撞击和震动） - Do not disassemble or deform the battery.（不要解剖和使电池变形） - Do not immerse in water.（不要把电池浸泡在水中） - Do not use the battery mixed with other different make, type, or model batteries. （不要和其它不同类型的电池混和使用） - Keep out of the reach of children.（放置电池于儿童不易接触的地方） . charge and discharge（充电和放电） - Battery must be charged in appropriate charger only. （电池必须用适当的充电器充电） - Never use a modified or damaged charger.（不要使用改装或损坏的充电器） - Do not leave battery in charger over 24 hours. （不要把电池放置于充电器超过24h） . storage(储存) - Store the battery in a cool, dry and well-ventilated area. （应把电池置于凉爽、干燥及通风良好的区域） . disposal（电池处理） - Regulations vary for different countries. Dispose of in accordance with local regulations.（电池处理要符合当地的规定） 7 Battery operation instruction（电池工作指南） 7.1 Charging（充电） Charging current：Cannot surpass the biggest charging current which in this specification book stipulated。 （充电电流：不能超过规格书上规定的最大充电电流） Charging voltage：Does not have to surpass the highest amount which in this specification book stipulated to decide the voltage。 （充电电压：不能超过规格书上规定的最大充电电压） Charge temperature：The battery must carry on the charge in the ambient temperature scope which this specification book stipulated。 （充电温度：电池充电必须在规格书规定环境温度范围内） |  |  |
| Uses the constant electric current and the constant voltage way charge, the prohibition reverse charges. If the battery positive electrode and the cathode meet instead, can damage the battery。（使用持续电流和电压方式进行充电，禁止反向充电，否则会损害电池） 7.2 Discharging current（放电电流） The discharging current does not have to surpass this specification book stipulation the biggest discharging current, the oversized electric current electric discharge can cause the battery capacity play to reduce and to cause the battery heat。 （不要超过本规格书上规定的最大放电电流，太大的电流放电会导致容量变小及使电池发热） 7.3 Electric discharge temperature（放电温度） The battery discharge must carry on in the ambient temperature scope which this specification book stipulated. （电池放电必须在本规格书规定的环境温度范围） 7.4 Over-discharges（过放电） After the short time excessively discharges charges immediately cannot affect the use, but the long time excessively discharges can cause the battery the performance, battery function losing. The battery long-term has not used, has the possibility to be able to be at because of its automatic flashover characteristic certain excessively discharges the condition, for prevented excessively discharges the occurrence, the battery should maintain the certain electric quantity。 (在短时间过放电然后立即充电不会影响电池的使用，但如果是长时间过放电会导致电池性能及电池功能丧失。电池长时间不使用，可能会有因它本身自动产生的电弧特性而必然的过放电情形，为防止电池过放电，电池应该保持一定的电量) 7. 5Storing the Batteries（储存电池） The battery should store in the product specification book stipulation temperature range. If has surpasses above for six months the long time storage, suggested you should carry on additional charge to the battery。（电池应该储存在本产品规格书中规定温度范围。如果储存时间超过六个月，建议对电池进行额外充电。） 8. Period of Warranty（保质期） The period of warranty is half a year from the date of shipment. Great Power guarantees to give a replacement in case of cells with defects proven due to manufacturing process instead of the customers abuse and misuse. （保质期从出货之日起半年。如果是制造过程的缺陷而不是用户错用滥用造成的，本公司确保更换） 9. Other The Chemical Reaction（其它的化学反应） Because batteries utilize a chemical reaction, battery performance will deteriorate over time even if stored for a long period of time without being used. In addition, if the various usage conditions such as charge, discharge, ambient temperature, etc. are not maintained within the specified ranges the life expectancy of the battery may be shortened or the device in which the battery is used may be damaged by electrolyte leakage. If the batteries cannot maintain a charge for long periods of time, even when they are charged correctly, this may indicate it is time to change the battery. （电池是利用化学反应产生电量，电池性能会随时间变差，即使电池长时间储存而不使用。另外，各种各样的使用方法，像充电、放电及环境温度，等等不能在本规格书规定的范围时的情形，会减小电 |  |  |
| 池的期望寿命，或者会使仪器设备由于电池漏液而损坏。即使充电正确，电池长时间不能再充电，那就要更换电池了。） 10.Note: Any other items which are not covered in this specification shall be agreed by both parties. （注意：任何本产品规格书未包含的其它条款，应由双方协议确定。） 11. 3D sketch for reference. The final product might be with difference, please refer to the final object. (三维示意图，仅供参考，实物可能会有出入，以最终实物为准） 12. Battery weight: 29.1KG Dimension: 352*263*225 mm |  |  |